## 6770686 Brazil
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 2
Distribution Company | Enel Distribuição Ceará
GS Type Code | GSS002/60
Material code | 6770686
Distribution network | LV
Type of Pole | HV
Nominal Length (m) | 9
Type | B
Description | 9m/300daN
Top Area (mm x mm) | 110 x 140 (± 5)
Butt Area (mm x mm) | 290 x 392 (± 5)
L2 (mm) | 1150 (± 20)
L3 (mm) | 75 (± 20)
L4 (mm) | 1525 (+20 -5)
Primary Conicity for rectangular poles section (narrow face) (mm/m) | 20
Secondary Conicity for rectangular poles section (wide face) (mm/m) | 28
Coating (mm) | 15 (20 on top)
Mass (Kg) | 750
Nominal Stress - Admissible Load (daN) | 300
Nominal Stress - Safety Factor | 2
Secondary Stress - Stress (daN) | 150
Secondary Stress - Safety Factor | 2
Breaking Strength (daN x m) | 600/300
Holes diameter (mm) | 19 (+2 -1)
Embedment lenght (m) | 1.5
Minimum lifetime (years) | 35

## 6770703 Brazil
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 2
Distribution Company | Enel Distribuição Ceará
GS Type Code | GSS002/66
Material code | 6770703
Distribution network | MV
Type of Pole | HV
Nominal Length (m) | 9
Type | B
Description | 9m/600daN
Top Area (mm x mm) | 110 x 140 (± 5)
Butt Area (mm x mm) | 290 x 392 (± 5)
L2 (mm) | 1000 (± 20)
L3 (mm) | 75 (± 20)
L4 (mm) | 3025 (+20 -5)
Primary Conicity for rectangular poles section (narrow face) (mm/m) | 20
Secondary Conicity for rectangular poles section (wide face) (mm/m) | 28
Coating (mm) | 15 (20 on top)
Mass (Kg) | 750
Nominal Stress - Admissible Load (daN) | 600
Nominal Stress - Safety Factor | 2
Secondary Stress - Stress (daN) | 300
Secondary Stress - Safety Factor | 2
Breaking Strength (daN x m) | 1200/600
Holes diameter (mm) | 19 (+2 -1)
Embedment lenght (m) | 1.5
Minimum lifetime (years) | 35

## 6770699 Brazil
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 2
Distribution Company | Enel Distribuição Ceará
GS Type Code | GSS002/67
Material code | 6770699
Distribution network | MV
Type of Pole | HV
Nominal Length (m) | 12
Type | B
Description | 12m/600daN
Top Area (mm x mm) | 110 x 140 (± 5)
Butt Area (mm x mm) | 350 x 476 (± 5)
L2 (mm) | 1300 (± 20)
L3 (mm) | 2775 (± 20)
L4 (mm) | 4525 (+20 -5)
Primary Conicity for rectangular poles section (narrow face) (mm/m) | 20
Secondary Conicity for rectangular poles section (wide face) (mm/m) | 28
Coating (mm) | 15 (20 on top)
Mass (Kg) | 1210
Nominal Stress - Admissible Load (daN) | 600
Nominal Stress - Safety Factor | 2
Secondary Stress - Stress (daN) | 300
Secondary Stress - Safety Factor | 2
Breaking Strength (daN x m) | 1200/600
Holes diameter (mm) | 19 (+2 -1)
Embedment lenght (m) | 1.8
Minimum lifetime (years) | 35

## 6770709 Brazil
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 2
Distribution Company | Enel Distribuição Ceará
GS Type Code | GSS002/68
Material code | 6770709
Distribution network | MV
Type of Pole | HV
Nominal Length (m) | 12
Type | B-1,5
Description | 12m/1000daN
Top Area (mm x mm) | 200 x 266 (± 5)
Butt Area (mm x mm) | 380 x 518 (± 5)
L2 (mm) | 1300 (± 20)
L3 (mm) | 2775 (± 20)
L4 (mm) | 4525 (+20 -5)
Primary Conicity for rectangular poles section (narrow face) (mm/m) | 20
Secondary Conicity for rectangular poles section (wide face) (mm/m) | 28
Coating (mm) | 15 (20 on top)
Mass (Kg) | 1900
Nominal Stress - Admissible Load (daN) | 1000
Nominal Stress - Safety Factor | 2
Secondary Stress - Stress (daN) | 500
Secondary Stress - Safety Factor | 2
Breaking Strength (daN x m) | 2000/1000
Holes diameter (mm) | 19 (+2 -1)
Embedment lenght (m) | 1.8
Minimum lifetime (years) | 35

## 4612613 Chile
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 2
Distribution Company | Enel Distribución Chile
GS Type Code | GSS002/78
Material code | 4612613
Distribution network | MV
Type of Pole | HV
Nominal Length (m) | 13.5
Top Area (mm x mm) | 165 x 180 (± 5)
Butt Area (mm x mm) | 300 x 450 (± 5)
Coating (mm) | 20
Mass (Kg) | 1880
Nominal Stress - Admissible Load (daN) | 660
Nominal Stress - Safety Factor | 2
Secondary Stress - Stress (daN) | 340
Secondary Stress - Safety Factor | 2
Breaking Strength (daN x m) | 1320
Holes diameter (mm) | 22
Embedment lenght (m) | 2.5
Minimum lifetime (years) | 35

## 6751776 Chile
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 2
Distribution Company | Enel Distribución Chile
GS Type Code | GSS002/76
Material code | 6751776
Distribution network | LV
Type of Pole | HV
Nominal Length (m) | 8.7
Top Area (mm x mm) | 120 x 120 (± 5)
Butt Area (mm x mm) | 220 x 350 (± 5)
Coating (mm) | 20
Mass (Kg) | 625
Nominal Stress - Admissible Load (daN) | 225
Nominal Stress - Safety Factor | 2
Secondary Stress - Stress (daN) | 60
Secondary Stress - Safety Factor | 2
Breaking Strength (daN x m) | 450
Holes diameter (mm) | 22
Embedment lenght (m) | 1.4
Minimum lifetime (years) | 35

## 6751778 Chile
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 2
Distribution Company | Enel Distribución Chile
GS Type Code | GSS002/77
Material code | 6751778
Distribution network | MV
Type of Pole | HV
Nominal Length (m) | 11.5
Top Area (mm x mm) | 150 x 150 (± 5)
Butt Area (mm x mm) | 250 x 430 (± 5)
Coating (mm) | 20
Mass (Kg) | 1100
Nominal Stress - Admissible Load (daN) | 267
Nominal Stress - Safety Factor | 2
Secondary Stress - Stress (daN) | 125
Secondary Stress - Safety Factor | 2
Breaking Strength (daN x m) | 534
Holes diameter (mm) | 22
Embedment lenght (m) | 2
Minimum lifetime (years) | 35

## 6751779 Chile
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 2
Distribution Company | Enel Distribución Chile
GS Type Code | GSS002/79
Material code | 6751779
Distribution network | MV
Type of Pole | HV
Nominal Length (m) | 15
Top Area (mm x mm) | 150 x 150 (± 5)
Butt Area (mm x mm) | 300 x 450 (± 5)
Coating (mm) | 20
Mass (Kg) | 2000
Nominal Stress - Admissible Load (daN) | 650
Nominal Stress - Safety Factor | 2
Secondary Stress - Stress (daN) | 240
Secondary Stress - Safety Factor | 2
Breaking Strength (daN x m) | 1300
Holes diameter (mm) | 22
Embedment lenght (m) | 2.5
Minimum lifetime (years) | 35

## 6756424 Peru
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 2
Distribution Company | Enel Distribución Peru
GS Type Code | GSS002/55
Material code | 6756424
Distribution network | LV
Type of Pole | HC
Nominal Length (m) | 11
Description | 11 / 200 / 2 / 150 / 315
Top Diameter (mm) | 150
Butt Diameter (mm) | 315
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 20
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 200
Nominal Stress - Safety Factor | 2
Breaking Strength (daN x m) | 400
Minimum lifetime (years) | 35

## 6756425 Peru
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 2
Distribution Company | Enel Distribución Peru
GS Type Code | GSS002/57
Material code | 6756425
Distribution network | MV / LV
Type of Pole | HC
Nominal Length (m) | 13
Description | 13 / 400 / 2,5 / 180 / 375
Top Diameter (mm) | 180
Butt Diameter (mm) | 375
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 25
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 400
Nominal Stress - Safety Factor | 2.5
Breaking Strength (daN x m) | 1000
Minimum lifetime (years) | 35

## 6756426 Peru
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 2
Distribution Company | Enel Distribución Peru
GS Type Code | GSS002/58
Material code | 6756426
Distribution network | MV / LV
Type of Pole | HC
Nominal Length (m) | 15
Description | 15 / 400 / 2,5 / 210 / 435
Top Diameter (mm) | 210
Butt Diameter (mm) | 435
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 25
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 400
Nominal Stress - Safety Factor | 2.5
Breaking Strength (daN x m) | 1000
Minimum lifetime (years) | 35

## 6785152 Peru
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 2
Distribution Company | Enel Distribución Peru
GS Type Code | GSS002/53
Material code | 6785152
Distribution network | LV
Type of Pole | HC
Nominal Length (m) | 8
Description | 8 / 200 / 2,0 / 150 / 270
Top Diameter (mm) | 150
Butt Diameter (mm) | 270
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 20
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 200
Nominal Stress - Safety Factor | 2
Breaking Strength (daN x m) | 400
Minimum lifetime (years) | 35

## 6785153 Peru
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 2
Distribution Company | Enel Distribución Peru
GS Type Code | GSS002/54
Material code | 6785153
Distribution network | LV
Type of Pole | HC
Nominal Length (m) | 9
Description | 9 / 200 / 2,0 / 150 / 285
Top Diameter (mm) | 150
Butt Diameter (mm) | 285
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 20
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 200
Nominal Stress - Safety Factor | 2
Breaking Strength (daN x m) | 400
Minimum lifetime (years) | 35

## 6762448 Colombia
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 4
Distribution Company | Enel Distribución Colombia
GS Type Code | GSS002/43
Material code | 6762448
Distribution network | LV
Type of Pole | HC/HCV
Nominal Length (m) | 12
Description | 12 x 510 AP
Top Diameter (mm) | 140
Butt Diameter (mm) | 320
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 20
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 200
Nominal Stress - Safety Factor | 2.5
Breaking Strength (daN x m) | 500
Minimum lifetime (years) | 35
Embedment lenght (m) | 1.8
Concrete minimum strength f'c (kg/cm²) | 245kg/cm² (350 kg/cm² prestressed)
Steel mimimum strenght fy (kg/cm²) | 4218 kg/cm² (60000psi)
Type of steel spirals or rings | Smooth or corrugated rod of 6.4 mm minimum diameter
Pole for network or public lighting | Public lighting
Compliant with specified markings and signals | Required
Type of steel for longitudinal reference | To be informed
Attached drawing with dimensions and markings | Required

## 6762449 Colombia
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 4
Distribution Company | Enel Distribución Colombia
GS Type Code | GSS002/39
Material code | 6762449
Distribution network | MV / LV
Type of Pole | HC/HCV
Nominal Length (m) | 10
Description | 10 x 510
Top Diameter (mm) | 140
Butt Diameter (mm) | 290
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 20
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 200
Nominal Stress - Safety Factor | 2.5
Breaking Strength (daN x m) | 500
Minimum lifetime (years) | 35
Embedment lenght (m) | 1.6
Concrete minimum strength f'c (kg/cm²) | 245kg/cm² (350 kg/cm² prestressed)
Steel mimimum strenght fy (kg/cm²) | 4218 kg/cm² (60000psi)
Type of steel spirals or rings | Smooth or corrugated rod of 6.4 mm minimum diameter
Pole for network or public lighting | Network
Compliant with specified markings and signals | Required
Type of steel for longitudinal reference | To be informed
Attached drawing with dimensions and markings | Required
Two holes of 1 " diameter at a distance of 20 cm from the top and 50 cm below the embedment line | Required

## 6762450 Colombia
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 4
Distribution Company | Enel Distribución Colombia
GS Type Code | GSS002/41
Material code | 6762450
Distribution network | MV / LV
Type of Pole | HC/HCV
Nominal Length (m) | 10
Description | 10 x 1050
Top Diameter (mm) | 170
Butt Diameter (mm) | 320
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 20
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 412
Nominal Stress - Safety Factor | 2.5
Breaking Strength (daN x m) | 1030
Minimum lifetime (years) | 35
Embedment lenght (m) | 1.6
Concrete minimum strength f'c (kg/cm²) | 245kg/cm² (350 kg/cm² prestressed)
Steel mimimum strenght fy (kg/cm²) | 4218 kg/cm² (60000psi)
Type of steel spirals or rings | Smooth or corrugated rod of 6.4 mm minimum diameter
Pole for network or public lighting | Network
Compliant with specified markings and signals | Required
Type of steel for longitudinal reference | To be informed
Attached drawing with dimensions and markings | Required
Two holes of 1 " diameter at a distance of 20 cm from the top and 50 cm below the embedment line | Required

## 6762451 Colombia
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 4
Distribution Company | Enel Distribución Colombia
GS Type Code | GSS002/42
Material code | 6762451
Distribution network | MV / LV
Type of Pole | HC/HCV
Nominal Length (m) | 12
Description | 12 x 510
Top Diameter (mm) | 140
Butt Diameter (mm) | 320
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 20
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 200
Nominal Stress - Safety Factor | 2.5
Breaking Strength (daN x m) | 500
Minimum lifetime (years) | 35
Embedment lenght (m) | 1.8
Concrete minimum strength f'c (kg/cm²) | 245kg/cm² (350 kg/cm² prestressed)
Steel mimimum strenght fy (kg/cm²) | 4218 kg/cm² (60000psi)
Type of steel spirals or rings | Smooth or corrugated rod of 6.4 mm minimum diameter
Pole for network or public lighting | Network
Compliant with specified markings and signals | Required
Type of steel for longitudinal reference | To be informed
Attached drawing with dimensions and markings | Required
Two holes of 1 " diameter at a distance of 20 cm from the top and 50 cm below the embedment line | Required

## 6762452 Colombia
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 4
Distribution Company | Enel Distribución Colombia
GS Type Code | GSS002/44
Material code | 6762452
Distribution network | MV / LV
Type of Pole | HC/HCV
Nominal Length (m) | 12
Description | 12 x 750
Top Diameter (mm) | 140
Butt Diameter (mm) | 320
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 20
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 294
Nominal Stress - Safety Factor | 2.5
Breaking Strength (daN x m) | 735
Minimum lifetime (years) | 35
Embedment lenght (m) | 1.8
Grounding - Plate or metallic element section | Min 78 mm2
Closed top of pole | Required
Concrete minimum strength f'c (kg/cm²) | 245kg/cm² (350 kg/cm² prestressed)
Steel mimimum strenght fy (kg/cm²) | 4218 kg/cm² (60000psi)
Type of steel spirals or rings | Smooth or corrugated rod of 6.4 mm minimum diameter
Pole for network or public lighting | Network
Compliant with specified markings and signals | Required
Type of steel for longitudinal reference | To be informed
Attached drawing with dimensions and markings | Required
Two holes of 1 " diameter at a distance of 20 cm from the top and 50 cm below the embedment line | Required

## 6762453 Colombia
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 4
Distribution Company | Enel Distribución Colombia
GS Type Code | GSS002/46
Material code | 6762453
Distribution network | MV / LV
Type of Pole | HC/HCV
Nominal Length (m) | 14
Description | 14 x 750
Top Diameter (mm) | 160
Butt Diameter (mm) | 370
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 20
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 294
Nominal Stress - Safety Factor | 2.5
Breaking Strength (daN x m) | 735
Minimum lifetime (years) | 35
Embedment lenght (m) | 2
Grounding - Plate or metallic element section | Min 78 mm2
Closed top of pole | Required
Concrete minimum strength f'c (kg/cm²) | 245kg/cm² (350 kg/cm² prestressed)
Steel mimimum strenght fy (kg/cm²) | 4218 kg/cm² (60000psi)
Type of steel spirals or rings | Smooth or corrugated rod of 6.4 mm minimum diameter
Pole for network or public lighting | Network
Compliant with specified markings and signals | Required
Type of steel for longitudinal reference | To be informed
Attached drawing with dimensions and markings | Required
Two holes of 1 " diameter at a distance of 20 cm from the top and 50 cm below the embedment line | Required

## 6762454 Colombia
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 4
Distribution Company | Enel Distribución Colombia
GS Type Code | GSS002/47
Material code | 6762454
Distribution network | LV
Type of Pole | HC/HCV
Nominal Length (m) | 14
Description | 14 x 750 AP
Top Diameter (mm) | 140
Butt Diameter (mm) | 370
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 20
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 294
Nominal Stress - Safety Factor | 2.5
Breaking Strength (daN x m) | 735
Minimum lifetime (years) | 35
Embedment lenght (m) | 2
Concrete minimum strength f'c (kg/cm²) | 245kg/cm² (350 kg/cm² prestressed)
Steel mimimum strenght fy (kg/cm²) | 4218 kg/cm² (60000psi)
Type of steel spirals or rings | Smooth or corrugated rod of 6.4 mm minimum diameter
Pole for network or public lighting | Public lighting
Compliant with specified markings and signals | Required
Type of steel for longitudinal reference | To be informed
Attached drawing with dimensions and markings | Required

## 6762457 Colombia
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 4
Distribution Company | Enel Distribución Colombia
GS Type Code | GSS002/40
Material code | 6762457
Distribution network | LV
Type of Pole | HC/HCV
Nominal Length (m) | 10
Description | 10 x 510 AP
Top Diameter (mm) | 170
Butt Diameter (mm) | 320
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 20
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 200
Nominal Stress - Safety Factor | 2.5
Breaking Strength (daN x m) | 500
Minimum lifetime (years) | 35
Embedment lenght (m) | 1.8
Concrete minimum strength f'c (kg/cm²) | 245kg/cm² (350 kg/cm² prestressed)
Steel mimimum strenght fy (kg/cm²) | 4218 kg/cm² (60000psi)
Type of steel spirals or rings | Smooth or corrugated rod of 6.4 mm minimum diameter
Pole for network or public lighting | Public lighting
Compliant with specified markings and signals | Required
Type of steel for longitudinal reference | To be informed
Attached drawing with dimensions and markings | Required

## 6762458 Colombia
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 4
Distribution Company | Enel Distribución Colombia
GS Type Code | GSS002/48
Material code | 6762458
Distribution network | MV / LV
Type of Pole | HC/HCV
Nominal Length (m) | 14
Description | 14 x 1050
Top Diameter (mm) | 190
Butt Diameter (mm) | 400
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 20
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 412
Nominal Stress - Safety Factor | 2.5
Breaking Strength (daN x m) | 1030
Minimum lifetime (years) | 35
Embedment lenght (m) | 2
Grounding - Plate or metallic element section | Min 78 mm2
Closed top of pole | Required
Concrete minimum strength f'c (kg/cm²) | 245kg/cm² (350 kg/cm² prestressed)
Steel mimimum strenght fy (kg/cm²) | 4218 kg/cm² (60000psi)
Type of steel spirals or rings | Smooth or corrugated rod of 6.4 mm minimum diameter
Pole for network or public lighting | Network
Compliant with specified markings and signals | Required
Type of steel for longitudinal reference | To be informed
Attached drawing with dimensions and markings | Required
Two holes of 1 " diameter at a distance of 20 cm from the top and 50 cm below the embedment line | Required

## 6762464 Colombia
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 4
Distribution Company | Enel Distribución Colombia
GS Type Code | GSS002/49
Material code | 6762464
Distribution network | MV / LV
Type of Pole | HC/HCV
Nominal Length (m) | 14
Description | 14 x 1350
Top Diameter (mm) | 200
Butt Diameter (mm) | 410
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 20
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 530
Nominal Stress - Safety Factor | 2.5
Breaking Strength (daN x m) | 1324
Minimum lifetime (years) | 35
Embedment lenght (m) | 2
Grounding - Plate or metallic element section | Min 78 mm2
Closed top of pole | Required
Concrete minimum strength f'c (kg/cm²) | 245kg/cm² (350 kg/cm² prestressed)
Steel mimimum strenght fy (kg/cm²) | 4218 kg/cm² (60000psi)
Type of steel spirals or rings | Smooth or corrugated rod of 6.4 mm minimum diameter
Pole for network or public lighting | Network
Compliant with specified markings and signals | Required
Type of steel for longitudinal reference | To be informed
Attached drawing with dimensions and markings | Required
Two holes of 1 " diameter at a distance of 20 cm from the top and 50 cm below the embedment line | Required

## 6762467 Colombia
Main Characteristics | Requested by Enel Group | Offered by Supplier | Note
Supplier | -
Factory | -
Global Standard | GSS002 rev. 4
Distribution Company | Enel Distribución Colombia
GS Type Code | GSS002/45
Material code | 6762467
Distribution network | MV / LV
Type of Pole | HC/HCV
Nominal Length (m) | 12
Description | 12 x 1050
Top Diameter (mm) | 190
Butt Diameter (mm) | 370
Conicity for Circular poles section (mm/m) | 15
Coating (mm) | 20
Mass (Kg) | -
Nominal Stress - Admissible Load (daN) | 412
Nominal Stress - Safety Factor | 2.5
Breaking Strength (daN x m) | 1030
Minimum lifetime (years) | 35
Embedment lenght (m) | 1.8
Grounding - Plate or metallic element section | Min 78 mm2
Closed top of pole | Required
Concrete minimum strength f'c (kg/cm²) | 245kg/cm² (350 kg/cm² prestressed)
Steel mimimum strenght fy (kg/cm²) | 4218 kg/cm² (60000psi)
Type of steel spirals or rings | Smooth or corrugated rod of 6.4 mm minimum diameter
Pole for network or public lighting | Network
Compliant with specified markings and signals | Required
Type of steel for longitudinal reference | To be informed
Attached drawing with dimensions and markings | Required
Two holes of 1 " diameter at a distance of 20 cm from the top and 50 cm below the embedment line | Required

## endesa (hidden)
| POSTES DE HORMIGÓN ARMADO VIBRADO (HV) (ENDESA) | [13 empty] | Precio Italia | 0.7 | Precio Hormigon | 411.9509
Resumen | Código |  | Descripción | Utilización | Altura (m) | Esfuerzo principal |  | Esfuerzo secundario |  | Momento de rotura a torsión (daN x m) | Masa (kg) | Medidas cogolla (mm x mm) | Estimación consumo anual (unidades) | Precio medio en península (€) | Estimación consumo anual (modificado) | Volumen Hormigón | Peso Hormigon | Peso Fe | Peso Total | Valor concreto | Valor Fe | Precio | Diferencia
filtro | [5 empty] | Esfuerzo (daN) | Coef. Seguridad | Esfuerzo (daN) | Coef. Seguridad | [6 empty] | m3 | kg | kg |  |  |  | Lista
| 6700355 | HV 250 R 9 | POSTE HORMIGON HV250R9 ETU-6703B | MT / BT | 9 | 250 | 2.5 | 160 | 2.25 |  |  | 110 x 145 | 29.6667 | 158.6671 | 0 | 0.28872 | 678.5 | 76.5 | 755 | 118.9399 | 53.55 | 172.4899 | -13.8228
endesa | 6700356 | HV 400 R 9 | POSTE HORMIGÓN HV400R9 ETU-6703B | MT / BT | 9 | 400 | 2.5 | 250 | 2.25 |  |  | 140 x 200 | 91 | 170.8767 | 91 | 0.37213 | 874.5 | 90.5 | 965 | 153.2983 | 63.35 | 216.6483 | -45.7716
endesa | 6700357 | HV 630 R 9 | POSTE HORMIGON HV630R9 ETU-6703B | MT / BT | 9 | 630 | 2.5 | 360 | 2.25 |  |  | 140 x 200 | 243 | 195.9514 | 0 | 0.3717 | 873.5 | 136.5 | 1010 | 153.123 | 95.55 | 248.673 | -52.7217
endesa | 6700358 | HV 800 R 9 | POSTE HORMIGON HV800R9 ETU-6703B | MT / BT | 9 | 800 | 2.5 | 400 | 2.25 |  |  | 140 x 200 | 198.6667 | 219.594 | 198.6667 | 0.37128 | 872.5 | 152.5 | 1025 | 152.9477 | 106.75 | 259.6977 | -40.1037
| 6700359 | HV 1000 R 9 | POSTE HORMIGON HV1000R9 ETU-6703B | MT / BT | 9 | 1000 | 2.5 | 500 | 2.25 | 540 |  | 170 x 255 | 54.6667 | 257.8629 | 0 | 0.46447 | 1091.5 | 158.5 | 1250 | 191.338 | 110.95 | 302.288 | -44.4251
endesa | 6700360 | HV 400 R 11 | POSTE HORMIGON HV400R11 ETU-6703B | MT / BT | 11 | 400 | 2.5 | 250 | 2.25 |  |  | 140 x 200 | 269 | 211.0359 | 269 | 0.50426 | 1185 | 120 | 1305 | 207.7284 | 84 | 291.7284 | -80.6925
endesa | 6700361 | HV 630 R 11 | POSTE HORMIGON HV630R11 ETU-6703B | MT / BT | 11 | 630 | 2.5 | 360 | 2.25 |  |  | 140 x 200 | 344.3333 | 240.1906 | 344.3333 | 0.51489 | 1210 | 170 | 1380 | 212.1109 | 119 | 331.1109 | -90.9203
endesa | 6700362 | HV 800 R 11 | POSTE HORMIGON HV800R11 ETU-6703B | MT / BT | 11 | 800 | 2.5 | 400 | 2.25 |  |  | 140 x 200 | 224.6667 | 266.2598 | 224.6667 | 0.5183 | 1218 | 197 | 1415 | 213.5133 | 137.9 | 351.4133 | -85.1535
endesa | 6700363 | HV 1000 R 11 | POSTE HORMIGON HV1000R11 ETU-6703B | MT / BT | 11 | 1000 | 2.5 | 500 | 2.25 | 540 |  | 170 x 255 | 257 | 324.9218 | 257 | 0.61489 | 1445 | 200 | 1645 | 253.306 | 140 | 393.306 | -68.3842
| 6700370 | HV 1600 R 11 | POSTE HORMIGON HV1600R11 ETU-6703B | MT / BT | 11 | 1600 | 2.5 | 600 | 2.25 | 540 |  | 170 x 255 | 48.6667 | 388.4283 | 0 | 0.59191 | 1391 | 299 | 1690 | 243.8399 | 209.3 | 453.1399 | -64.7116
| 6700371 | HV 400 R 13 | POSTE HORMIGON HV400R13 ETU-6703B | MT / BT | 13 | 400 | 2.5 | 250 | 2.25 |  |  | 140 x 200 | 17.6667 | 276.5223 | 0 | 0.65298 | 1534.5 | 140.5 | 1675 | 268.9952 | 98.35 | 367.3452 | -90.8228
| 6700372 | HV 630 R 13 | POSTE HORMIGON HV630R13 ETU-6703B | MT / BT | 13 | 630 | 2.5 | 360 | 2.25 |  |  | 140 x 200 | 47 | 303.6082 | 0 | 0.63383 | 1489.5 | 205.5 | 1695 | 261.1068 | 143.85 | 404.9568 | -101.3486
| 6700373 | HV 800 R 13 | POSTE HORMIGON HV800R13 ETU-6703B | MT / BT | 13 | 800 | 2.5 | 400 | 2.25 |  |  | 140 x 200 | 78 | 343.3506 | 0 | 0.61894 | 1454.5 | 250.5 | 1705 | 254.9713 | 175.35 | 430.3213 | -86.9707
endesa | 6700374 | HV 1000 R 13 | POSTE HORMIGON HV1000R13 ETU-6703B | MT / BT | 13 | 1000 | 2.5 | 500 | 2.25 | 540 |  | 170 x 255 | 186.3333 | 404.0045 | 186.3333 | 0.77328 | 1817.2 | 277.8 | 2095 | 318.552 | 194.46 | 513.012 | -109.0075
endesa | 6700375 | HV 1600 R 13 | POSTE HORMIGON HV1600R13 ETU-6703B | MT / BT | 13 | 1600 | 2.5 | 600 | 2.25 | 540 |  | 170 x 255 | 75.3333 | 523.988 | 75.3333 | 0.75021 | 1763 | 382 | 2145 | 309.0508 | 267.4 | 576.4508 | -52.4628
| 6700670 | HV 250 R 11 | POSTE HORMIGON HV250R11 ETU-6703B | MT / BT | 11 | 250 | 2.5 | 160 | 2.25 |  |  | 110 x 145 | 3.6667 | 176.1904 | 0 | 0.39617 | 931 | 89 | 1020 | 163.2027 | 62.3 | 225.5027 | -49.3123
| 6700671 | HV 250 R 13 | POSTE HORMIGON HV250R13 ETU-6703B | MT / BT | 13 | 250 | 2.5 | 160 | 2.25 |  |  | 110 x 145 | 2 | 228.8289 | 0 | 0.5166 | 1214 | 116 | 1330 | 212.8121 | 81.2 | 294.0121 | -65.1832
| 6701501 | HV 800 R 15 | POSTE HORMIGÓN HV800R15 ETU-6703B | MT / BT | 15 | 800 | 2.5 | 400 | 2.25 |  |  | 140 x 200 | 21 | 425.4938 | 0 | 0.76681 | 1802 | 323 | 2125 | 315.8875 | 226.1 | 541.9875 | -116.4936
| 6701502 | HV 1000 R 15 | POSTE HORMIGÓN HV1000R15 ETU-6703B | MT / BT | 15 | 1000 | 2.5 | 500 | 2.25 | 540 |  | 170 x 255 | 41.3333 | 477.1165 | 0 | 0.96043 | 2257 | 343 | 2600 | 395.6482 | 240.1 | 635.7482 | -158.6317
Conicidad cara estrecha = 13 ± 2 mm/m
Conicidad cara ancha = 21 ± 2 mm/m
Recubrimiento mínimo concreto 15 mm y 20 mm
Los precios en las islas soportan un significativo impacto del coste de transporte. "Incremento medio sobre coste medio en península"
|  |  | Baleares |  | Canarias
|  |  | 43% |  | 95%
Los precios en la Península dependen de la zona georáfica de destino, por lo que los precios indicados son valores medios de los resultados obtenidos en la última licitación para los diversos territorios.

## enel (hidden)
| POSTES DE HORMIGÓN ARMADO CENTRIFUGADO (CAC) - ENEL | [12 empty] | Precio KG Acero | 0.9 | [5 empty] | Precio Hormigon
Resumen | Código | Descripción | Utilización | Altura (m) | Tiro de prueba |  | Esfuerzo secundario |  | Momento de rotura a torsión (daN x m) | Masa (Kg) | Medidas cima / base (mm x mm) | Estimación consumo anual (unidades) | Precio medio (€) | Estimación consumo anual (modificado) | Volumen Hormigón | Peso Hormigon | Peso Fe | Peso Total | Valor concreto | Valor Fe | 411.9509 | Precio | Diferencia
[5 empty] | Esfuerzo (daN) | Coef. Seguridad | Esfuerzo (daN) | Coef. Seguridad | [6 empty] | m3 | kg | kg | kg |  |  |  | Lista
enel | 230212 | PALO CAC - 10 / A / 12 UE | BT | 10 | 412 | 2.5 | 412 |  |  | 620 | 120 / 270 | 4860 | 189.9294 | 0 | 0.239 | 562 | 58 | 620 | 137.7294 | 52.2 | 576.2737 | 150.6563 | 39.2732
enel | 230222 | PALO CAC - 10 / B / 14 UE | BT | 10 | 550 | 2.5 | 550 |  |  | 720 | 140 / 290 | 2539 | 211.31 | 7399 | 0.275 | 646 | 72 | 718 | 146.51 | 64.8 | 532.7635 | 178.0865 | 33.2235
enel | 230232 | PALO CAC - 10 / C / 18 UE | BT | 10 | 824 | 2.5 | 824 |  |  | 950 | 180 / 330 | 3337 | 254.5409 | 0 | 0.359 | 844 | 92 | 936 | 171.7409 | 82.8 | 478.3869 | 230.6904 | 23.8505
enel | 230242 | PALO CAC - 10 / D / 20 UE | BT | 10 | 1091 | 2.5 | 1091 |  |  | 1120 | 200 / 350 | 4684 | 284.987 | 8021 | 0.419 | 985 | 116 | 1101 | 180.587 | 104.4 | 430.9952 | 277.0074 | 7.9795
enel | 230252 | PALO CAC - 10 / E / 24 UE | BT | 10 | 1638 | 2.5 | 1638 |  |  | 1450 | 240 / 390 | 4532 | 351.2105 | 4532 | 0.54 | 1269 | 153 | 1422 | 213.5105 | 137.7 | 395.3898 | 360.1535 | -8.943
enel | 230262 | PALO CAC - 10 / F / 27 UE | BT | 10 | 2188 | 2.5 | 2188 |  |  | 1700 | 270 / 420 | 1447 | 409.4326 | 1447 | 0.648 | 1523 | 192 | 1715 | 236.6326 | 172.8 | 365.1738 | 439.7442 | -30.3116
enel | 230272 | PALO CAC - 10 / G / 31 UE | BT | 10 | 3286 | 2.5 | 3286 |  |  | 2100 | 310 / 460 | 175 | 511.1943 | 175 | 0.796 | 1871 | 262 | 2133 | 275.3943 | 235.8 | 345.9727 | 563.7129 | -52.5186
enel | 230224 | PALO CAC - 12 / B / 14 UE | BT | 12 | 550 | 2.5 | 550 |  |  | 1000 | 140 / 320 | 923 | 266.9177 | 923 | 0.38 | 893 | 97 | 990 | 179.6177 | 87.3 | 472.6781 | 243.8413 | 23.0763
enel | 230234 | PALO CAC - 12 / C / 18 UE | BT/MT | 12 | 824 | 2.5 | 824 |  |  | 1270 | 180 / 360 | 621 | 318.2287 | 0 | 0.493 | 1159 | 127 | 1286 | 203.9287 | 114.3 | 413.6484 | 317.3918 | 0.83687
enel | 230244 | PALO CAC - 12 / D / 20 UE | BT/MT | 12 | 1099 | 2.5 | 1099 |  |  | 1460 | 200 / 380 | 603 | 361.8955 | 1224 | 0.552 | 1297 | 157 | 1454 | 220.5955 | 141.3 | 399.6296 | 368.6969 | -6.8014
enel | 230254 | PALO CAC - 12 / E / 24 UE | BT/MT | 12 | 1648 | 2.5 | 1648 |  |  | 1900 | 240 / 420 | 382 | 460.3979 | 382 | 0.745 | 1751 | 211 | 1962 | 270.4979 | 189.9 | 363.0844 | 496.8034 | -36.4055
enel | 230264 | PALO CAC - 12 / F / 27 UE | BT/MT | 12 | 2198 | 2.5 | 2198 |  |  | 2250 | 270 / 450 | 332 | 544.0241 | 332 | 0.824 | 1936 | 264 | 2200 | 306.4241 | 237.6 | 371.8739 | 577.0475 | -33.0235
enel | 230274 | PALO CAC - 12 / G / 31 UE | BT/MT | 12 | 3296 | 2.5 | 3296 |  |  | 2700 | 310 / 490 | 341 | 655.4135 | 341 | 1.007 | 2366 | 352 | 2718 | 338.6135 | 316.8 | 336.2597 | 731.6346 | -76.2211
enel | 230276 | PALO CAC - 12 / H / 32 UE | BT/MT | 12 | 6280 | 2.5 | 6280 |  |  | 3600 | 320 / 500 | 50 | 1098.98 | 0 | 1.272 | 2989 | 584 | 3573 | 573.38 | 525.6 | 450.7704 | 1049.6016 | 49.3784
| 230245 | PALO CAC - 14 / D / 20 UE | BT/MT | 14 | 1099 | 2.5 | 1099 |  |  | 1910 | 200 / 410 | 8 | 475.75 | 0 | 0.732 | 1720 | 198 | 1918 | 297.55 | 178.2 | 406.4891 | 479.7481 | -3.9981
| 230255 | PALO CAC - 14 / E / 24 UE | BT/MT | 14 | 1648 | 2.5 | 1648 |  |  | 2400 | 240 / 450 | 3 | 600.3333 | 0 | 0.921 | 2164 | 278 | 2442 | 350.1333 | 250.2 | 380.1665 | 629.6068 | -29.2735
| 230265 | PALO CAC - 14 / F / 27 UE | BT/MT | 14 | 2198 | 2.5 | 2198 |  |  | 2800 | 270 / 480 | 2 | 667.5 | 0 | 1.015 | 2385 | 344 | 2729 | 357.9 | 309.6 | 352.6108 | 727.7302 | -60.2302
| 230275 | PALO CAC - 14 / G / 31 UE | BT/MT | 14 | 3296 | 2.5 | 3296 |  |  | 3400 | 310 / 520 | 8 | 834.5 | 0 | 1.234 | 2900 | 457 | 3357 | 423.2 | 411.3 | 342.9498 | 919.6474 | -85.1474
Resistencia concreto > 540 daN/cm²
Recubrimiento de concreto >= 15 mm

## latam (hidden)
POSTES DE HORMIGÓN ARMADO VIBRADO - LATAM
Resumen | Código | Descripción | Utilización | Altura (m) | Esfuerzo principal |  | Esfuerzo secundario |  | Momento de rotura a torsión (daN x m) | Masa (kg) (**) | Medidas cogolla (mm x mm) | Estimación consumo anual (unidades) | Precio medio (€) | Estimación consumo anual (modificado) | Peso | Peso | empresa latam
[5 empty] | Esfuerzo (daN) | Coef. Seguridad | Esfuerzo (daN) | Coef. Seguridad | [6 empty] | Hormigon | Fierro | AMPLA | COELCE | CODENSA | CHILECTRA | EDELNOR
chilectra | 6751776 | Poste Concreto de 8,7m ; 220 daN | BT | 8,7 | 220 | 1.75 | 60 | 1.75 |  | 625 | 120 x 120 | 3600 | 87.0846 | 0 | [5 empty] | X
coelce | 6770683 | Poste Concreto de 9m ; 150 daN | BT | 9 | 150 | 2 | 75 | 2 |  | 470 | 100 x 120 | 20951 | 85.2964 | 20951 |  |  |  | X |  |  | X
ampla | 6771952 | Poste Concreto de 9m ; 200 daN | BT | 9 | 200 | 2 | 100 | 2 |  | 470 | 100 x 120 | 273 | 89.2362 | 0 |  |  | X
coelce | 6770686 | Poste Concreto de 9m ; 300 daN | BT | 9 | 300 | 2 | 150 | 2 |  | 750 | 110 x 140 | 26378 | 125.7061 | #REF! |  |  |  | X |  |  | X
ampla | 6771953 | Poste Concreto de 9m ; 400 daN | BT | 9 | 400 | 2 | 200 | 2 |  | 750 | 110 x 140 | 1637 | 116.2792 | 1637 |  |  | X
coelce | 6770796 | Poste Concreto de 10,5m ; 150 daN | MT | 10,5 | 150 | 2 | 75 | 2 |  | 600 | 100 x 120 | 22995 | 112.4361 | 30188 |  |  |  | X
coelce | 6770797 | Poste Concreto de 10,5m ; 300 daN | MT | 10,5 | 300 | 2 | 150 | 2 |  | 980 | 110 x 140 | 17794 | 158.2232 | 18717 |  |  |  | X
coelce | 6770798 | Poste Concreto de 10,5m ; 600 daN | MT | 10,5 | 600 | 2 | 300 | 2 |  | 980 | 110 x 140 | 8213 | 207.2889 | 31208 |  |  |  | X
ampla | 6771954 | Poste Concreto de 11m ; 200 daN | MT | 11 | 200 | 2 | 100 | 2 |  | 980 | 100 x 120 | 1393 | 113.8639 | #REF! |  |  | X
ampla | 6771955 | Poste Concreto de 11m ; 400 daN | MT | 11 | 400 | 2 | 200 | 2 |  | 1050 | 110 x 140 | 20593 | 158.7521 | 20593 |  |  | X |  |  |  | X
ampla | 6799790 | Poste Concreto de 11m ; 600 daN | MT | 11 | 600 | 2 | 300 | 2 |  | 1050 | 110 x 140 | 3272 | 191.5908 | 3272 |  |  | X
chilectra | 6751778 | Poste Concreto de 11,5m ; 300 daN | MT | 11,5 | 300 | 1.75 | 75 | 1.75 |  | 1100 | 150 x 150 | 4010 | 158.9231 | 0 | [5 empty] | X
coelce | 6770694 | Poste Concreto de 12m ; 300 daN | MT | 12 | 300 | 2 | 150 | 2 |  | 1210 | 110 x 140 | 10463 | 186.5239 | 31056 |  |  |  | X | X
coelce | 6771957 | Poste Concreto de 12m ; 400 daN | MT | 12 | 400 | 2 | 200 | 2 |  | 1210 | 110 x 140 | 3313 | 193.2991 | 3313 |  |  | X |  | X
ampla/coelce | 6771958 | Poste Concreto de 12m ; 600 daN | MT | 12 | 600 | 2 | 300 | 2 |  | 1210 | 110 x 140 | 7193 | 236.2439 | 7193 |  |  | X | X
|  |  |  | 13 | 400 | 2 | 200 | 2 |  | 1400 | 110 x 140 | 923 | 169.1152 | 923 | [6 empty] | X
( * ) CORRESPONDE A REQUERIMIENTOS DE POSTES EN CODENSA
(**) LOS PESOS SON REFERENCIALES Y NO DE CUMPLIMIENTO ESPECIFICO
|  | Conicidad cara estrecha = 13 ± 2 mm/m | [7 empty] | Poste Troncocónico - Pretensado (CODENSA)
Conicidad cara ancha = 21 ± 2 mm/m
Recubrimiento de concreto >= 15 mm / 20 mm / 25 mm