## First page
Annex 3
List of the points of the data base

## Remote controls
Remote Controls | Description of the point | S/E | Point Type ENDESA | IOA ENDESA | Point Type ENEL | IOA ENEL | Comando 0 SC(0) DC(1) | Comando 1 SC(1) DC(2) | RTU8 | RTU16 | LVCB | SD | SSCB | REC | Notes
general | Automatisms Disabled |  |  |  | SC | 1 |  | DISABLE | x | x
| Normal Status of the Automatisms |  | SC | 10069 | SC | 2 |  | NSA | x | x |  |  |  |  | Restoration of the normal status of the automatisms
| Spontaneous Calls enabled |  |  |  | SC | 3 | DISABLE | ENABLE | x | x
| Reset of the pre-lock status / Reset of the Automatisms |  |  |  | SC | 4 |  | RESET | x | x |  |  |  |  | Reset control which acts on all of the automatisms on the RTU, i.e. the automatisms of all of the switchgears.
| Spare |  |  |  | SC | 150 |  |  | x | x |  |  |  |  | Available for future changes
ODM | OP command SG 1 | x |  |  | SC | 5 |  | OPEN | x | x | OP | OP | OP | OP
| CL command SG 1 | x |  |  | SC | 6 |  | CLOSE | x | x | CL | CL | CL | CL
| OP command SG 2 | x |  |  | SC | 7 |  | OPEN | x | x | OP | OP | OP | 79X_E | 79X_E/79X_D of the REC for the Center corresponds to the command of reclosure of SD and SSCB
| CL command SG 2 | x |  |  | SC | 8 |  | CLOSE | x | x | CL | CL | CL | 79X_D
| OP command SG 3 | x |  |  | SC | 9 |  | OPEN | x | x | OP | OP | OP | OP
| CL command SG 3 | x |  |  | SC | 10 |  | CLOSE | x | x | CL | CL | CL | CL
| OP command SG 4 | x |  |  | SC | 11 |  | OPEN | x | x | OP | OP | OP | 79X_E
| CL command SG 4 | x |  |  | SC | 12 |  | CLOSE | x | x | CL | CL | CL | 79X_D
| OP command SG 5 | x |  |  | SC | 13 |  | OPEN | x | x | OP | OP | OP | OP
| CL command SG 5 | x |  |  | SC | 14 |  | CLOSE | x | x | CL | CL | CL | CL
| OP command SG 6 | x |  |  | SC | 15 |  | OPEN | x | x | OP | OP | OP | 79X_E
| CL command SG 6 | x |  |  | SC | 16 |  | CLOSE | x | x | CL | CL | CL | 79X_D
| OP command SG 7 | x |  |  | SC | 17 |  | OPEN | x | x | OP | OP | OP | OP
| CL command SG 7 | x |  |  | SC | 18 |  | CLOSE | x | x | CL | CL | CL | CL
| OP command SG 8 | x |  |  | SC | 19 |  | OPEN | x | x | OP | OP | OP | 79X_E
| CL command SG 8 | x |  |  | SC | 20 |  | CLOSE | x | x | CL | CL | CL | 79X_D
| OP command SG 9 | x |  |  | SC | 1005 |  | OPEN |  | x | OP | OP | OP | OP
| CL command SG 9 | x |  |  | SC | 1006 |  | CLOSE |  | x | CL | CL | CL | CL
| OP command SG 10 | x |  |  | SC | 1007 |  | OPEN |  | x | OP | OP | OP | 79X_E
| CL command SG 10 | x |  |  | SC | 1008 |  | CLOSE |  | x | CL | CL | CL | 79X_D
| OP command SG 11 | x |  |  | SC | 1009 |  | OPEN |  | x | OP | OP | OP | OP
| CL command SG 11 | x |  |  | SC | 1010 |  | CLOSE |  | x | CL | CL | CL | CL
| OP command SG 12 | x |  |  | SC | 1011 |  | OPEN |  | x | OP | OP | OP | 79X_E
| CL command SG 12 | x |  |  | SC | 1012 |  | CLOSE |  | x | CL | CL | CL | 79X_D
| OP command SG 13 | x |  |  | SC | 1013 |  | OPEN |  | x | OP | OP | OP | OP
| CL command SG 13 | x |  |  | SC | 1014 |  | CLOSE |  | x | CL | CL | CL | CL
| OP command SG 14 | x |  |  | SC | 1015 |  | OPEN |  | x | OP | OP | OP | 79X_E
| CL command SG 14 | x |  |  | SC | 1016 |  | CLOSE |  | x | CL | CL | CL | 79X_D |  | DIR | Direction of the protection
| OP command SG 15 | x |  |  | SC | 1017 |  | OPEN |  | x | OP | OP | OP | OP |  | DC | Double command
| CL command SG 15 | x |  |  | SC | 1018 |  | CLOSE |  | x | CL | CL | CL | CL |  | SC | Single Command
| OP command SG 16 | x |  |  | SC | 1019 |  | OPEN |  | x | OP | OP | OP | 79X_E |  | MFD | Manual Fault Detection
| CL command SG 16 | x |  |  | SC | 1020 |  | CLOSE |  | x | CL | CL | CL | 79X_D |  | MFDD | Manual Fault Detection Disabled
| command SG 1 | x | DC | 15001 |  |  | OPEN | CLOSE | x | x | OP/CL | OP/CL | OP/CL
| command SG 2 | x | DC | 15002 |  |  | OPEN | CLOSE | x | x | OP/CL | OP/CL | OP/CL
| command SG 3 | x | DC | 15003 |  |  | OPEN | CLOSE | x | x | OP/CL | OP/CL | OP/CL
| command SG 4 | x | DC | 15004 |  |  | OPEN | CLOSE | x | x | OP/CL | OP/CL | OP/CL
| command SG 5 | x | DC | 15005 |  |  | OPEN | CLOSE | x | x | OP/CL | OP/CL | OP/CL
| command SG 6 | x | DC | 15006 |  |  | OPEN | CLOSE | x | x | OP/CL | OP/CL | OP/CL
| command SG 7 | x | DC | 15007 |  |  | OPEN | CLOSE | x | x | OP/CL | OP/CL | OP/CL
| command SG 8 | x | DC | 15008 |  |  | OPEN | CLOSE | x | x | OP/CL | OP/CL | OP/CL
| command SG 9 | x | DC | 15009 |  |  | OPEN | CLOSE |  | x | OP/CL | OP/CL | OP/CL
| command SG 10 | x | DC | 15010 |  |  | OPEN | CLOSE |  | x | OP/CL | OP/CL | OP/CL
| command SG 11 | x | DC | 15011 |  |  | OPEN | CLOSE |  | x | OP/CL | OP/CL | OP/CL
| command SG 12 | x | DC | 15012 |  |  | OPEN | CLOSE |  | x | OP/CL | OP/CL | OP/CL
| command SG 13 | x | DC | 15013 |  |  | OPEN | CLOSE |  | x | OP/CL | OP/CL | OP/CL
| command SG 14 | x | DC | 15014 |  |  | OPEN | CLOSE |  | x | OP/CL | OP/CL | OP/CL
| command SG 15 | x | DC | 15015 |  |  | OPEN | CLOSE |  | x | OP/CL | OP/CL | OP/CL
| command SG 16 | x | DC | 15016 |  |  | OPEN | CLOSE |  | x | OP/CL | OP/CL | OP/CL
automatisms | control of the automatism 1 |  |  |  | SC | 21 | DISABLED | ENABLED | x | x | AUT | AUT | AUT
| control of the automatism 2 |  |  |  | SC | 22 | DISABLED | ENABLED | x | x | AUT | AUT | AUT
| control of the automatism 3 |  |  |  | SC | 23 | DISABLED | ENABLED | x | x | AUT | AUT | AUT
| control of the automatism 4 |  |  |  | SC | 24 | DISABLED | ENABLED | x | x | AUT | AUT | AUT
| control of the automatism 5 |  |  |  | SC | 25 | DISABLED | ENABLED | x | x | AUT | AUT | AUT
| control of the automatism 6 |  |  |  | SC | 26 | DISABLED | ENABLED | x | x | AUT | AUT | AUT
| control of the automatism 7 |  |  |  | SC | 27 | DISABLED | ENABLED | x | x | AUT | AUT | AUT
| control of the automatism 8 |  |  |  | SC | 28 | DISABLED | ENABLED | x | x | AUT | AUT | AUT
| control of the automatism 9 |  |  |  | SC | 1021 | DISABLED | ENABLED |  | x | AUT | AUT | AUT
| control of the automatism 10 |  |  |  | SC | 1022 | DISABLED | ENABLED |  | x | AUT | AUT | AUT
| control of the automatism 11 |  |  |  | SC | 1023 | DISABLED | ENABLED |  | x | AUT | AUT | AUT
| control of the automatism 12 |  |  |  | SC | 1024 | DISABLED | ENABLED |  | x | AUT | AUT | AUT
| control of the automatism 13 |  |  |  | SC | 1025 | DISABLED | ENABLED |  | x | AUT | AUT | AUT
| control of the automatism 14 |  |  |  | SC | 1026 | DISABLED | ENABLED |  | x | AUT | AUT | AUT
| control of the automatism 15 |  |  |  | SC | 1027 | DISABLED | ENABLED |  | x | AUT | AUT | AUT
| control of the automatism 16 |  |  |  | SC | 1028 | DISABLED | ENABLED |  | x | AUT | AUT | AUT
| control of reclosure 1 |  |  |  | SC | 201 | DISABLED | ENABLED | x | x |  | MFD | MFD |  | MFDD=!MFD (MFD=Manual Fault Detection)
| control of reclosure 2 |  |  |  | SC | 202 | DISABLED | ENABLED | x | x |  | MFD | MFD
| control of reclosure 3 |  |  |  | SC | 203 | DISABLED | ENABLED | x | x |  | MFD | MFD
| control of reclosure 4 |  |  |  | SC | 204 | DISABLED | ENABLED | x | x |  | MFD | MFD
| control of reclosure 5 |  |  |  | SC | 205 | DISABLED | ENABLED | x | x |  | MFD | MFD
| control of reclosure 6 |  |  |  | SC | 206 | DISABLED | ENABLED | x | x |  | MFD | MFD
| control of reclosure 7 |  |  |  | SC | 207 | DISABLED | ENABLED | x | x |  | MFD | MFD
| control of reclosure 8 |  |  |  | SC | 208 | DISABLED | ENABLED | x | x |  | MFD | MFD
| control of reclosure 9 |  |  |  | SC | 1201 | DISABLED | ENABLED |  | x |  | MFD | MFD
| control of reclosure 10 |  |  |  | SC | 1202 | DISABLED | ENABLED |  | x |  | MFD | MFD
| control of reclosure 11 |  |  |  | SC | 1203 | DISABLED | ENABLED |  | x |  | MFD | MFD
| control of reclosure 12 |  |  |  | SC | 1204 | DISABLED | ENABLED |  | x |  | MFD | MFD
| control of reclosure 13 |  |  |  | SC | 1205 | DISABLED | ENABLED |  | x |  | MFD | MFD
| control of reclosure 14 |  |  |  | SC | 1206 | DISABLED | ENABLED |  | x |  | MFD | MFD
| control of reclosure 15 |  |  |  | SC | 1207 | DISABLED | ENABLED |  | x |  | MFD | MFD
| control of reclosure 16 |  |  |  | SC | 1208 | DISABLED | ENABLED |  | x |  | MFD | MFD
| reset of the automatism 1 |  |  |  | SC | 209 |  | RESET | x | x | Reset | Reset | Reset | Reset
| reset of the automatism 2 |  |  |  | SC | 210 |  | RESET | x | x | Reset | Reset | Reset
| reset of the automatism 3 |  |  |  | SC | 211 |  | RESET | x | x | Reset | Reset | Reset | Reset
| reset of the automatism 4 |  |  |  | SC | 212 |  | RESET | x | x | Reset | Reset | Reset
| reset of the automatism 5 |  |  |  | SC | 213 |  | RESET | x | x | Reset | Reset | Reset | Reset
| reset of the automatism 6 |  |  |  | SC | 214 |  | RESET | x | x | Reset | Reset | Reset
| reset of the automatism 7 |  |  |  | SC | 215 |  | RESET | x | x | Reset | Reset | Reset | Reset
| reset of the automatism 8 |  |  |  | SC | 216 |  | RESET | x | x | Reset | Reset | Reset
| reset of the automatism 9 |  |  |  | SC | 1209 |  | RESET |  | x | Reset | Reset | Reset | Reset
| reset of the automatism 10 |  |  |  | SC | 1210 |  | RESET |  | x | Reset | Reset | Reset
| reset of the automatism 11 |  |  |  | SC | 1211 |  | RESET |  | x | Reset | Reset | Reset | Reset
| reset of the automatism 12 |  |  |  | SC | 1212 |  | RESET |  | x | Reset | Reset | Reset
| reset of the automatism 13 |  |  |  | SC | 1213 |  | RESET |  | x | Reset | Reset | Reset | Reset
| reset of the automatism 14 |  |  |  | SC | 1214 |  | RESET |  | x | Reset | Reset | Reset
| reset of the automatism 15 |  |  |  | SC | 1215 |  | RESET |  | x | Reset | Reset | Reset | Reset
| reset of the automatism 16 |  |  |  | SC | 1216 |  | RESET |  | x | Reset | Reset | Reset
| ungrounded neutral 1 |  |  |  | SC | 217 | DISABLED | ENABLED | x | x |  | UN | UN |  | These controls modify what is defined in the configuration file, in correspondence of the paramenter DEF_SN of the automatism for the given switchgear
| ungrounded neutral 2 |  |  |  | SC | 218 | DISABLED | ENABLED | x | x |  | UN | UN
| ungrounded neutral 3 |  |  |  | SC | 219 | DISABLED | ENABLED | x | x |  | UN | UN
| ungrounded neutral 4 |  |  |  | SC | 220 | DISABLED | ENABLED | x | x |  | UN | UN
| ungrounded neutral 5 |  |  |  | SC | 221 | DISABLED | ENABLED | x | x |  | UN | UN
| ungrounded neutral 6 |  |  |  | SC | 222 | DISABLED | ENABLED | x | x |  | UN | UN
| ungrounded neutral 7 |  |  |  | SC | 223 | DISABLED | ENABLED | x | x |  | UN | UN
| ungrounded neutral 8 |  |  |  | SC | 224 | DISABLED | ENABLED | x | x |  | UN | UN
| ungrounded neutral 9 |  |  |  | SC | 1217 | DISABLED | ENABLED |  | x |  | UN | UN
| ungrounded neutral 10 |  |  |  | SC | 1218 | DISABLED | ENABLED |  | x |  | UN | UN
| ungrounded neutral 11 |  |  |  | SC | 1219 | DISABLED | ENABLED |  | x |  | UN | UN
| ungrounded neutral 12 |  |  |  | SC | 1220 | DISABLED | ENABLED |  | x |  | UN | UN
| ungrounded neutral 13 |  |  |  | SC | 1221 | DISABLED | ENABLED |  | x |  | UN | UN
| ungrounded neutral 14 |  |  |  | SC | 1222 | DISABLED | ENABLED |  | x |  | UN | UN
| ungrounded neutral 15 |  |  |  | SC | 1223 | DISABLED | ENABLED |  | x |  | UN | UN
| ungrounded neutral 16 |  |  |  | SC | 1224 | DISABLED | ENABLED |  | x |  | UN | UN
| function of compensated neutral 1 |  |  |  | SC | 225 | DISABLED | ENABLED | x | x |  | CN | CN |  | These controls modify what is defined in the configuration file, in correspondence of the paramenter DEF_SA of the automatism for the given switchgear.The DISABLED control corresponds to the type FFPI (Function of Faul+P55t Passage Indicator)
| function of compensated neutral 2 |  |  |  | SC | 226 | DISABLED | ENABLED | x | x |  | CN | CN
| function of compensated neutral 3 |  |  |  | SC | 227 | DISABLED | ENABLED | x | x |  | CN | CN
| function of compensated neutral 4 |  |  |  | SC | 228 | DISABLED | ENABLED | x | x |  | CN | CN
| function of compensated neutral 5 |  |  |  | SC | 229 | DISABLED | ENABLED | x | x |  | CN | CN
| function of compensated neutral 6 |  |  |  | SC | 230 | DISABLED | ENABLED | x | x |  | CN | CN
| function of compensated neutral 7 |  |  |  | SC | 231 | DISABLED | ENABLED | x | x |  | CN | CN
| function of compensated neutral 8 |  |  |  | SC | 232 | DISABLED | ENABLED | x | x |  | CN | CN
| function of compensated neutral 9 |  |  |  | SC | 1225 | DISABLED | ENABLED |  | x |  | CN | CN
| function of compensated neutral 10 |  |  |  | SC | 1226 | DISABLED | ENABLED |  | x |  | CN | CN
| function of compensated neutral 11 |  |  |  | SC | 1227 | DISABLED | ENABLED |  | x |  | CN | CN
| function of compensated neutral 12 |  |  |  | SC | 1228 | DISABLED | ENABLED |  | x |  | CN | CN
| function of compensated neutral 13 |  |  |  | SC | 1229 | DISABLED | ENABLED |  | x |  | CN | CN
| function of compensated neutral 14 |  |  |  | SC | 1230 | DISABLED | ENABLED |  | x |  | CN | CN
| function of compensated neutral 15 |  |  |  | SC | 1231 | DISABLED | ENABLED |  | x |  | CN | CN
| function of compensated neutral 16 |  |  |  | SC | 1232 | DISABLED | ENABLED |  | x |  | CN | CN
DIR | DIR command 1 |  |  |  | SC | 29 | OUTGOING | INCOMING | x | x |  | DIR | DIR | DIR | DIR of the REC for the Center corresponds to the automatism control of the SD and SSCB
| DIR command 2 |  |  |  | SC | 30 | OUTGOING | INCOMING | x | x |  | DIR | DIR | P_E/P_D
| DIR command 3 |  |  |  | SC | 31 | OUTGOING | INCOMING | x | x |  | DIR | DIR | DIR
| DIR command 4 |  |  |  | SC | 32 | OUTGOING | INCOMING | x | x |  | DIR | DIR | P_E/P_D
| DIR command 5 |  |  |  | SC | 33 | OUTGOING | INCOMING | x | x |  | DIR | DIR | DIR
| DIR command 6 |  |  |  | SC | 34 | OUTGOING | INCOMING | x | x |  | DIR | DIR | P_E/P_D
| DIR command 7 |  |  |  | SC | 35 | OUTGOING | INCOMING | x | x |  | DIR | DIR | DIR
| DIR command 8 |  |  |  | SC | 36 | OUTGOING | INCOMING | x | x |  | DIR | DIR | P_E/P_D
| DIR command 9 |  |  |  | SC | 1029 | OUTGOING | INCOMING |  | x |  | DIR | DIR | DIR
| DIR command 10 |  |  |  | SC | 1030 | OUTGOING | INCOMING |  | x |  | DIR | DIR | P_E/P_D
| DIR command 11 |  |  |  | SC | 1031 | OUTGOING | INCOMING |  | x |  | DIR | DIR | DIR
| DIR command 12 |  |  |  | SC | 1032 | OUTGOING | INCOMING |  | x |  | DIR | DIR | P_E/P_D
| DIR command 13 |  |  |  | SC | 1033 | OUTGOING | INCOMING |  | x |  | DIR | DIR | DIR
| DIR command 14 |  |  |  | SC | 1034 | OUTGOING | INCOMING |  | x |  | DIR | DIR | P_E/P_D
| DIR command 15 |  |  |  | SC | 1035 | OUTGOING | INCOMING |  | x |  | DIR | DIR | DIR
| DIR command 16 |  |  |  | SC | 1036 | OUTGOING | INCOMING |  | x |  | DIR | DIR | P_E/P_D

## Remote Signals
Remote signals | Point Description | Point Type ENDESA | IOA ENDESA | state 0 SP(0) DP(1) | State 1 SP(1) DP(2) | Point Type ENEL | IOA ENEL | state 0 SP(0) DP(1) | State 1 SP(1) DP(2) | RTU8 | RTU16 | LVCB | SD | SSCB | REC | Notes
General | Alarm for substation door opening | SP | 10010 | DISABLED | ENABLED | SP | 1 | DISABLED | ENABLED | x | x
| Transformer SD open | SP | 10011 | CLOSED | OPEN | SP | 2 | CLOSED | OPEN | x | x
Plant | Substation under remote control | DP | 15000 | TELECONTROL | LOCAL | SP | 3 | DISABLED | ENABLED | x | x
| Substation under local control |  |  |  |  | SP | 4 | DISABLED | ENABLED | x | x
| Mains failure | SP | 10012 | DISABLED | ENABLED | SP | 5 | DISABLED | ENABLED | x | x
| Motors failure | SP | 10013 | DISABLED | ENABLED | SP | 6 | DISABLED | ENABLED | x | x
| Rectifiers failure | SP | 10014 | DISABLED | ENABLED | SP | 7 | DISABLED | ENABLED | x | x
| Low Vcc | SP | 10015 | DISABLED | ENABLED | SP | 8 | DISABLED | ENABLED | x | x
| Battery fail | SP | 10016 | DISABLED | ENABLED | SP | 150 | DISABLED | ENABLED | x | x
Spare | Remote signal spare 1 | SP | 10033 | Disabled | Enabled | SP | 9 | Disabled | Enabled | x | x | Trp | LVI | LVI | RCP | For the REC, Dir is equal to the point " autom. direction sw, utilized by SD and SSCB. The spare RS , for the REC and the SSCB, can assume a value different from the provided in the column. In particular, for the REC the spare RS can be utilized as LVI.
| Remote signal spare 2 | SP | 10034 | Disabled | Enabled | SP | 10 | Disabled | Enabled | x | x | Trp | LVI | LVI | Dir
| Remote signal spare 3 | SP | 10035 | Disabled | Enabled | SP | 11 | Disabled | Enabled | x | x | Trp | LVI | LVI | RCP
| Remote signal spare 4 | SP | 10036 | Disabled | Enabled | SP | 12 | Disabled | Enabled | x | x | Trp | LVI | LVI | Dir
| Remote signal spare 5 | SP | 10037 | Disabled | Enabled | SP | 13 | Disabled | Enabled | x | x | Trp | LVI | LVI | RCP
| Remote signal spare 6 | SP | 10038 | Disabled | Enabled | SP | 14 | Disabled | Enabled | x | x | Trp | LVI | LVI | Dir
| Remote signal spare 7 | SP | 10039 | Disabled | Enabled | SP | 15 | Disabled | Enabled | x | x | Trp | LVI | LVI | RCP
| Remote signal spare 8 | SP | 10040 | Disabled | Enabled | SP | 16 | Disabled | Enabled | x | x | Trp | LVI | LVI | Dir
| Remote signal spare 9 | SP | 10057 | Disabled | Enabled | SP | 1009 | Disabled | Enabled |  | x | Trp | LVI | LVI | RCP
| Remote signal spare 10 | SP | 10058 | Disabled | Enabled | SP | 1010 | Disabled | Enabled |  | x | Trp | LVI | LVI | Dir
| Remote signal spare 11 | SP | 10059 | Disabled | Enabled | SP | 1011 | Disabled | Enabled |  | x | Trp | LVI | LVI | RCP
| Remote signal spare 12 | SP | 10060 | Disabled | Enabled | SP | 1012 | Disabled | Enabled |  | x | Trp | LVI | LVI | Dir
| Remote signal spare 13 | SP | 10061 | Disabled | Enabled | SP | 1013 | Disabled | Enabled |  | x | Trp | LVI | LVI | RCP
| Remote signal spare 14 | SP | 10062 | Disabled | Enabled | SP | 1014 | Disabled | Enabled |  | x | Trp | LVI | LVI | Dir
| Remote signal spare 15 | SP | 10063 | Disabled | Enabled | SP | 1015 | Disabled | Enabled |  | x | Trp | LVI | LVI | RCP
| Remote signal spare 16 | SP | 10064 | Disabled | Enabled | SP | 1016 | Disabled | Enabled |  | x | Trp | LVI | LVI | Dir
SG Position | Status of the SG 1 | DP | 15001 | OPEN | CLOSED | DP | 1 | OPEN | CLOSED | x | x | Open/Closed | Open/Closed | Open/Closed | Open/Closed
| Status of the SG 2 | DP | 15002 | OPEN | CLOSED | DP | 2 | OPEN | CLOSED | x | x | Open/Closed | Open/Closed | Open/Closed | 79X_E/79X_D | 79X_E/79X_D (status 0=Disabl,1=IEnabl) are equalt to the point MFD sw and MFDD of the SD and the SSCB.
| Status of the SG 3 | DP | 15003 | OPEN | CLOSED | DP | 3 | OPEN | CLOSED | x | x | Open/Closed | Open/Closed | Open/Closed | Open/Closed
| Status of the SG 4 | DP | 15004 | OPEN | CLOSED | DP | 4 | OPEN | CLOSED | x | x | Open/Closed | Open/Closed | Open/Closed | 79X_E/79X_D
| Status of the SG 5 | DP | 15005 | OPEN | CLOSED | DP | 5 | OPEN | CLOSED | x | x | Open/Closed | Open/Closed | Open/Closed | Open/Closed
| Status of the SG 6 | DP | 15006 | OPEN | CLOSED | DP | 6 | OPEN | CLOSED | x | x | Open/Closed | Open/Closed | Open/Closed | 79X_E/79X_D
| Status of the SG 7 | DP | 15007 | OPEN | CLOSED | DP | 7 | OPEN | CLOSED | x | x | Open/Closed | Open/Closed | Open/Closed | Open/Closed
| Status of the SG 8 | DP | 15008 | OPEN | CLOSED | DP | 8 | OPEN | CLOSED | x | x | Open/Closed | Open/Closed | Open/Closed | 79X_E/79X_D
| Status of the SG 9 | DP | 15009 | OPEN | CLOSED | DP | 1001 | OPEN | CLOSED |  | x | Open/Closed | Open/Closed | Open/Closed | Open/Closed
| Status of the SG 10 | DP | 15010 | OPEN | CLOSED | DP | 1002 | OPEN | CLOSED |  | x | Open/Closed | Open/Closed | Open/Closed | 79X_E/79X_D
| Status of the SG 11 | DP | 15011 | OPEN | CLOSED | DP | 1003 | OPEN | CLOSED |  | x | Open/Closed | Open/Closed | Open/Closed | Open/Closed
| Status of the SG 12 | DP | 15012 | OPEN | CLOSED | DP | 1004 | OPEN | CLOSED |  | x | Open/Closed | Open/Closed | Open/Closed | 79X_E/79X_D
| Status of the SG 13 | DP | 15013 | OPEN | CLOSED | DP | 1005 | OPEN | CLOSED |  | x | Open/Closed | Open/Closed | Open/Closed | Open/Closed
| Status of the SG 14 | DP | 15014 | OPEN | CLOSED | DP | 1006 | OPEN | CLOSED |  | x | Open/Closed | Open/Closed | Open/Closed | 79X_E/79X_D
| Status of the SG 15 | DP | 15015 | OPEN | CLOSED | DP | 1007 | OPEN | CLOSED |  | x | Open/Closed | Open/Closed | Open/Closed | Open/Closed
| Status of the SG 16 | DP | 15016 | OPEN | CLOSED | DP | 1008 | OPEN | CLOSED |  | x | Open/Closed | Open/Closed | Open/Closed | 79X_E/79X_D
Fault passage Indicators | FPI of the zero sequence current 1 | SP | 10017 | DISABLED | ENABLED | SP | 17 | DISABLED | ENABLED | x | x |  | FPI_ZS | FPI_ZS | 67
| FPI of the overcurrent 1 | SP | 10018 | DISABLED | ENABLED | SP | 18 | DISABLED | ENABLED | x | x |  | FPI_OC | FPI_OC | 51
| FPI of the zero sequence current 2 | SP | 10019 | DISABLED | ENABLED | SP | 19 | DISABLED | ENABLED | x | x |  | FPI_ZS | FPI_ZS | P_ E/P_D | P_ E/P_D (status 0=DISABLED, 1=ENABLED) is equal to the point "sw of enabling automatism" utilized by SD and SSCB. The signals FPI_ZS or FPI_OC can be utilized by a Recloser because the Sapre RS are utilized.
| FPI of the overcurrent 2 | SP | 10020 | DISABLED | ENABLED | SP | 20 | DISABLED | ENABLED | x | x |  | FPI_OC | FPI_OC | PaWa
| FPI of the zero sequence current 3 | SP | 10021 | DISABLED | ENABLED | SP | 21 | DISABLED | ENABLED | x | x |  | FPI_ZS | FPI_ZS | 67
| FPI of the overcurrent 3 | SP | 10022 | DISABLED | ENABLED | SP | 22 | DISABLED | ENABLED | x | x |  | FPI_OC | FPI_OC | 51
| FPI of the zero sequence current 4 | SP | 10023 | DISABLED | ENABLED | SP | 23 | DISABLED | ENABLED | x | x |  | FPI_ZS | FPI_ZS | P_ E/P_D
| FPI of the overcurrent 4 | SP | 10024 | DISABLED | ENABLED | SP | 24 | DISABLED | ENABLED | x | x |  | FPI_OC | FPI_OC | PaWa
| FPI of the zero sequence current 5 | SP | 10025 | DISABLED | ENABLED | SP | 25 | DISABLED | ENABLED | x | x |  | FPI_ZS | FPI_ZS | 67
| FPI of the overcurrent 5 | SP | 10026 | DISABLED | ENABLED | SP | 26 | DISABLED | ENABLED | x | x |  | FPI_OC | FPI_OC | 51
| FPI of the zero sequence current 6 | SP | 10027 | DISABLED | ENABLED | SP | 27 | DISABLED | ENABLED | x | x |  | FPI_ZS | FPI_ZS | P_ E/P_D
| FPI of the overcurrent 6 | SP | 10028 | DISABLED | ENABLED | SP | 28 | DISABLED | ENABLED | x | x |  | FPI_OC | FPI_OC | PaWa
| FPI of the zero sequence current 7 | SP | 10029 | DISABLED | ENABLED | SP | 29 | DISABLED | ENABLED | x | x |  | FPI_ZS | FPI_ZS | 67
| FPI of the overcurrent 7 | SP | 10030 | DISABLED | ENABLED | SP | 30 | DISABLED | ENABLED | x | x |  | FPI_OC | FPI_OC | 51
| FPI of the zero sequence current 8 | SP | 10031 | DISABLED | ENABLED | SP | 31 | DISABLED | ENABLED | x | x |  | FPI_ZS | FPI_ZS | P_ E/P_D
| FPI of the overcurrent 8 | SP | 10032 | DISABLED | ENABLED | SP | 32 | DISABLED | ENABLED | x | x |  | FPI_OC | FPI_OC | PaWa
| FPI of the zero sequence current 9 | SP | 10041 | DISABLED | ENABLED | SP | 1017 | DISABLED | ENABLED |  | x |  | FPI_ZS | FPI_ZS | 67
| FPI of the overcurrent 9 | SP | 10042 | DISABLED | ENABLED | SP | 1018 | DISABLED | ENABLED |  | x |  | FPI_OC | FPI_OC | 51
| FPI of the zero sequence current 10 | SP | 10043 | DISABLED | ENABLED | SP | 1019 | DISABLED | ENABLED |  | x |  | FPI_ZS | FPI_ZS | P_ E/P_D
| FPI of the overcurrent 10 | SP | 10044 | DISABLED | ENABLED | SP | 1020 | DISABLED | ENABLED |  | x |  | FPI_OC | FPI_OC | PaWa
| FPI of the zero sequence current 11 | SP | 10045 | DISABLED | ENABLED | SP | 1021 | DISABLED | ENABLED |  | x |  | FPI_ZS | FPI_ZS | 67
| FPI of the overcurrent 11 | SP | 10046 | DISABLED | ENABLED | SP | 1022 | DISABLED | ENABLED |  | x |  | FPI_OC | FPI_OC | 51
| FPI of the zero sequence current 12 | SP | 10047 | DISABLED | ENABLED | SP | 1023 | DISABLED | ENABLED |  | x |  | FPI_ZS | FPI_ZS | P_ E/P_D
| FPI of the overcurrent 12 | SP | 10048 | DISABLED | ENABLED | SP | 1024 | DISABLED | ENABLED |  | x |  | FPI_OC | FPI_OC | PaWa
| FPI of the zero sequence current 13 | SP | 10049 | DISABLED | ENABLED | SP | 1025 | DISABLED | ENABLED |  | x |  | FPI_ZS | FPI_ZS | 67
| FPI of the overcurrent 13 | SP | 10050 | DISABLED | ENABLED | SP | 1026 | DISABLED | ENABLED |  | x |  | FPI_OC | FPI_OC | 51
| FPI of the zero sequence current 14 | SP | 10051 | DISABLED | ENABLED | SP | 1027 | DISABLED | ENABLED |  | x |  | FPI_ZS | FPI_ZS | P_ E/P_D
| FPI of the overcurrent 14 | SP | 10052 | DISABLED | ENABLED | SP | 1028 | DISABLED | ENABLED |  | x |  | FPI_OC | FPI_OC | PaWa
| FPI of the zero sequence current 15 | SP | 10053 | DISABLED | ENABLED | SP | 1029 | DISABLED | ENABLED |  | x |  | FPI_ZS | FPI_ZS | 67
| FPI of the overcurrent 15 | SP | 10054 | DISABLED | ENABLED | SP | 1030 | DISABLED | ENABLED |  | x |  | FPI_OC | FPI_OC | 51
| FPI of the zero sequence current 16 | SP | 10055 | DISABLED | ENABLED | SP | 1031 | DISABLED | ENABLED |  | x |  | FPI_ZS | FPI_ZS | P_ E/P_D
| FPI of the overcurrent 16 | SP | 10056 | DISABLED | ENABLED | SP | 1032 | DISABLED | ENABLED |  | x |  | FPI_OC | FPI_OC | PaWa
Automatisms | Enabling automatism 1 |  |  |  |  | SP | 33 | DISABLED | ENABLED | x | x | x | x | x |  | For the Center, it corresponds to P_ E/P_D of the REC
| Enabling automatism 2 |  |  |  |  | SP | 34 | DISABLED | ENABLED | x | x | x | x | x
| Enabling automatism 3 |  |  |  |  | SP | 35 | DISABLED | ENABLED | x | x | x | x | x
| Enabling automatism 4 |  |  |  |  | SP | 36 | DISABLED | ENABLED | x | x | x | x | x
| Enabling automatism 5 |  |  |  |  | SP | 37 | DISABLED | ENABLED | x | x | x | x | x
| Enabling automatism 6 |  |  |  |  | SP | 38 | DISABLED | ENABLED | x | x | x | x | x
| Enabling automatism 7 |  |  |  |  | SP | 39 | DISABLED | ENABLED | x | x | x | x | x
| Enabling automatism 8 |  |  |  |  | SP | 40 | DISABLED | ENABLED | x | x | x | x | x
| Enabling automatism 9 |  |  |  |  | SP | 1033 | DISABLED | ENABLED |  | x | x | x | x
| Enabling automatism 10 |  |  |  |  | SP | 1034 | DISABLED | ENABLED |  | x | x | x | x
| Enabling automatism 11 |  |  |  |  | SP | 1035 | DISABLED | ENABLED |  | x | x | x | x
| Enabling automatism 12 |  |  |  |  | SP | 1036 | DISABLED | ENABLED |  | x | x | x | x
| Enabling automatism 13 |  |  |  |  | SP | 1037 | DISABLED | ENABLED |  | x | x | x | x
| Enabling automatism 14 |  |  |  |  | SP | 1038 | DISABLED | ENABLED |  | x | x | x | x
| Enabling automatism 15 |  |  |  |  | SP | 1039 | DISABLED | ENABLED |  | x | x | x | x
| Enabling automatism 16 |  |  |  |  | SP | 1040 | DISABLED | ENABLED |  | x | x | x | x
DIR | direction of the RGDAT 1 |  |  |  |  | SP | 41 | OUTGOING | INCOMING | x | x |  | x | x |  | It corresponds to ISV of the REC for the Center
| direction of the RGDAT 2 |  |  |  |  | SP | 42 | OUTGOING | INCOMING | x | x |  | x | x
| direction of the RGDAT 3 |  |  |  |  | SP | 43 | OUTGOING | INCOMING | x | x |  | x | x
| direction of the RGDAT 4 |  |  |  |  | SP | 44 | OUTGOING | INCOMING | x | x |  | x | x
| direction of the RGDAT 5 |  |  |  |  | SP | 45 | OUTGOING | INCOMING | x | x |  | x | x
| direction of the RGDAT 6 |  |  |  |  | SP | 46 | OUTGOING | INCOMING | x | x |  | x | x
| direction of the RGDAT 7 |  |  |  |  | SP | 47 | OUTGOING | INCOMING | x | x |  | x | x
| direction of the RGDAT 8 |  |  |  |  | SP | 48 | OUTGOING | INCOMING | x | x |  | x | x
| direction of the RGDAT 9 |  |  |  |  | SP | 1041 | OUTGOING | INCOMING |  | x |  | x | x
| direction of the RGDAT 10 |  |  |  |  | SP | 1042 | OUTGOING | INCOMING |  | x |  | x | x
| direction of the RGDAT 11 |  |  |  |  | SP | 1043 | OUTGOING | INCOMING |  | x |  | x | x
| direction of the RGDAT 12 |  |  |  |  | SP | 1044 | OUTGOING | INCOMING |  | x |  | x | x
| direction of the RGDAT 13 |  |  |  |  | SP | 1045 | OUTGOING | INCOMING |  | x |  | x | x
| direction of the RGDAT 14 |  |  |  |  | SP | 1046 | OUTGOING | INCOMING |  | x |  | x | x
| direction of the RGDAT 15 |  |  |  |  | SP | 1047 | OUTGOING | INCOMING |  | x |  | x | x
| direction of the RGDAT 16 |  |  |  |  | SP | 1048 | OUTGOING | INCOMING |  | x |  | x | x
Diagnostics | Fault of the Base Unit | SP | 10065 | DISABLED | ENABLED | SP | 105 | DISABLED | ENABLED | x | x
| 1/N Control Alarm | SP | 10066 | DISABLED | ENABLED | SP | 106 | DISABLED | ENABLED | x | x
| Alarm of RC relays mixed up | SP | 10067 | DISABLED | ENABLED | SP | 107 | DISABLED | ENABLED | x | x
| Events Buffer full | SP | 10068 | DISABLED | ENABLED | SP | 108 | DISABLED | ENABLED | x | x
| Status of the spontaneous calls enabling | SP | 10069 | DISABLED | ENABLED | SP | 109 | DISABLED | ENABLED | x | x
| Failure of the Expansion RS module |  |  |  |  | SP | 110 | DISABLED | ENABLED
| Failure of the Expansion RC module |  |  |  |  | SP | 111 | DISABLED | ENABLED
| Failure of the Expansion TM module |  |  |  |  | SP | 112 | DISABLED | ENABLED
| Failure of the Expansion DO module |  |  |  |  | SP | 113 | DISABLED | ENABLED
| Expansion RS module Missing |  |  |  |  | SP | 114 | DISABLED | ENABLED
| Expansion RC module Missing |  |  |  |  | SP | 115 | DISABLED | ENABLED
| Expansion TM module Missing |  |  |  |  | SP | 116 | DISABLED | ENABLED
| Expansion DO module Missing |  |  |  |  | SP | 117 | DISABLED | ENABLED
| II overflow threshold of the measurements Trend |  |  |  |  | SP | 118 | DISABLED | ENABLED | x | x
| I overflow threshold of the measurements Trend |  |  |  |  | SP | 119 | DISABLED | ENABLED | x | x
| Gruppo in posizione non configurata |  |  |  |  | SP | 120 | DISABLED | ENABLED
| Rules of configuration |  |  |  |  | SP | 121 | PRESENTE | ASSENTE | x | x
| Sent local control of buffer dowload |  |  |  |  | SP | 151 | DISABLED | ENABLED | x | x
| Substation Automatims disabled |  |  |  |  | SP | 152 | DISABLED | ENABLED | x | x
| Opening SD from pc in the substation |  |  |  |  | SP | 153 | DISABLED | ENABLED | x | x
| Wrong syntax of the file of configuration |  |  |  |  | SP | 154 | DISABLED | ENABLED | x | x
| Wrong semantic of the file of configuration |  |  |  |  | SP | 155 | DISABLED | ENABLED | x | x
| Wrong communication of the second telephone number of the Center |  |  |  |  | SP | 156 | DISABLED | ENABLED | x | x
| Wrong communication of the first telephone number of the Center |  |  |  |  | SP | 157 | DISABLED | ENABLED | x | x
| Errore comunicazione terzo numero telefono di centro | SP |  | ASSENTE | PRESENTE |  | 158 | ASSENTE | PRESENTE | x | x

## Measurements
Measurements | Point description | Point Type | IOA ENDESA | IOA ENEL | RTU8 | RTU16 | Notes
Spare | Spare TM 1 | ME (CYCLIC) | 30001 | 1 | x | x
| Spare TM 2 | ME (CYCLIC) | 30002 | 2 | x | x
| Spare TM 3 | ME (CYCLIC) | 30003 | 3 | x | x
| Spare TM 4 | ME (CYCLIC) | 30004 | 4 | x | x
| Spare TM 5 | ME (CYCLIC) | 30005 | 5 | x | x
| Spare TM 6 | ME (CYCLIC) | 30006 | 6 | x | x
| Spare TM 7 | ME (CYCLIC) | 30007 | 7 | x | x
| Spare TM 8 | ME (CYCLIC) | 30008 | 8 | x | x
| Spare TM 9 | ME (CYCLIC) | 30009 | 1001 |  | x
| Spare TM 10 | ME (CYCLIC) | 30010 | 1002 |  | x
| Spare TM 11 | ME (CYCLIC) | 30011 | 1003 |  | x
| Spare TM 12 | ME (CYCLIC) | 30012 | 1004 |  | x
| Spare TM 13 | ME (CYCLIC) | 30013 | 1005 |  | x
| Spare TM 14 | ME (CYCLIC) | 30014 | 1006 |  | x
| Spare TM 15 | ME (CYCLIC) | 30015 | 1007 |  | x
| Spare TM 16 | ME (CYCLIC) | 30016 | 1008 |  | x
| TM Tamb | ME (CYCLIC) | 30000 | 201 | x | x
Trend | 10' average value of the spare TM 1 | FTRANS |  | 21 | x | x
| 10' average value of the spare TM 2 | FTRANS |  | 22 | x | x
| 10' average value of the spare TM 3 | FTRANS |  | 23 | x | x
| 10' average value of the spare TM 4 | FTRANS |  | 24 | x | x
| 10' average value of the spare TM 5 | FTRANS |  | 25 | x | x
| 10' average value of the spare TM 6 | FTRANS |  | 26 | x | x
| 10' average value of the spare TM 7 | FTRANS |  | 27 | x | x
| 10' average value of the spare TM 8 | FTRANS |  | 28 | x | x
| 10' average value of the spare TM 9 | FTRANS |  | 29 |  | x
| 10' average value of the spare TM 10 | FTRANS |  | 30 |  | x
| 10' average value of the spare TM 11 | FTRANS |  | 31 |  | x
| 10' average value of the spare TM 12 | FTRANS |  | 32 |  | x
| 10' average value of the spare TM 13 | FTRANS |  | 33 |  | x
| 10' average value of the spare TM 14 | FTRANS |  | 34 |  | x
| 10' average value of the spare TM 15 | FTRANS |  | 35 |  | x
| 10' average value of the spare TM 16 | FTRANS |  | 36 |  | x
| 10' average value of the TM Tamb | FTRANS |  | 37 | x | x
Others | Code of the Manifacturer | ME (SPONT) | 39996 | 501 | x | x | Finmek=2, Selta=3, Ducati=4, Areva=5, Siemens=6, Col=7, Abb=8, Alstom=9, Advanced Devices=10, Sindi=12
| Version of the SW Boot/Eprom | ME (SPONT) | 39997 | 502 | x | x | Format X.YY
| Version of the Application SW of the RTU | ME (SPONT) | 39998 | 503 | x | x | Format X.YY
| Version Dbase | ME (SPONT) | 39999 |  | x | x